## TOWNS for report
Discharge Name | Rec Water | Current Permitted Dry Weather Flow (m3/d | Flow headroom m3/d | Housing Capacity (115l/h/d & 2.4 people/house) | Housing Allocation | Current Ammonia / BOD / Phosphate | Future BOD / Ammonia / Phosphate - ‘no deterioration’ | Future BOD / Ammonia / Phosphate - current WFD class status | Future BOD / Ammonia / Phosphate - good WFD status | Conclusions / Comments
Coalport | River Severn | 17700 | 2347 | 8503 | 5714 | 10, 25, - | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. No further modelling carried out.
Crudgington | River Strine | 16 | No Measured Flow Data | n/a | 0 |  | n/a | n/a | n/a | No Growth Planned
Edgmond | Pipe Strine | 590 | 224.75 | 814.3116 | 74 | 3, 15, - | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. Modelling indicates that maintenance of current WFD class may require permit limits tighter than currently deemed achieveable should environmental deterioration occur.
Ellerdine | Lakemoor Brook | 20 | No Measured Flow Data | n/a | 0 |  | n/a | n/a | n/a | No Growth Planned
High Ercall | Trib River Roden | 210 | 107.5625 | 389.7192 | 106 | - , 80, - | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. No further modelling carried out.
Newport | Strine Brook | 2500 | 319.5 | 1157.6087 | 1309 | 3, 15, 2 | 0.5 , 2.5 , 1.3 | 0.6 , 4.8 , 0.1 | n/a , n/a , 0.1 | Increased DWF would be required to accomodate growth. This would trigger permit limits tighter than those currently deemed reliably achieveable.
Rushmoor | River Tern | 23523 | 7369.25 | 26700.1812 | 7879 | 5, 15, 2 | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. Modelling indicates that maintenance of current WFD class may require permit limits tighter than currently deemed achieveable should environmental deterioration occur.
Sambrook | River Meese | 49 | No Measured Flow Data | n/a | 32 |  | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. No further modelling carried out.
Shrewsbury | River Severn | 20838 | 3839.25 | 13910.3261 | 114 | 10, 25, - | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. No further modelling carried out.
Sugdon | Trib of the River Roden | 8 | No Measured Flow Data | n/a | 0 |  | n/a | n/a | n/a | No Growth Planned
Walcot | Trib of River Tern | 17 | No Measured Flow Data | n/a | 0 |  | n/a | n/a | n/a | No Growth Planned
Waters Upton | River Tern | 8 | No Measured Flow Data | n/a | 7 |  | n/a | n/a | n/a | Growth can potentially be accepted within current flow limit. No further modelling carried out.