## Sewage Treatment
Local Authority Water Cycle Study
Potential impact of proposed developments on sewage treatment works
Date
Note: These are desktop assessments using readily available information and have not been subjected to detailed hydraulic analysis
[22 empty] | Data from D041i2 - Original Study |  |  | Data for Amec Foster Wheeler assessment:
Key
No data
[7 empty] | Significant | Not expected to be an issue | No land or other constraints preventing expansion
[7 empty] | Limited | Marginal concern subject to size of development | Limited potential to provide additional capacity
[7 empty] | Minimal | Probable issue | No scope to provide additional capacity
Sewage Treatment Works Name | OS Grid Ref |  | Current PE | Current / observed dry weather flow (m3/d) | Estimated spare hydraulic capacity | Estimated spare hydraulic dwellingsPE | Estimate headroom based on current quality performance (RAG) | Future quality issues (RAG) | Physical constraints regarding provision of additional treatment capacity (RAG) | Any other comments | Receiving Water course | River Catch ment | Current Consent Information | [11 empty] | Additional dwellings (residential) |  |  |  | Additional employment
| Eastings | Northings |  |  | PE | Dwellings (@ 2.4hd/dwelling) | [6 empty] | Consent Reference | FFT (m3/d) | FFT -l/s | DWF (m3/d) | Amm (Summer) | Amm (Winter) | BOD (mg/l) | SS (mg/l) | P | Current PE | Current / observed dry weather flow (m3/d) | DWF - current consent (m3/d) | committed: under construction | committed: not started | Committed: resolution to grant | Allocated | Committed *dwelling* | Allocated (estimated FTE converted to dwelling)
Coalport | 370791 | 301539 | 78991 |  | Z | =Z/2.4 |  |  |  | AMP6 capital maintenance scheme - will incorprate growth as required | River Severn |  | S/02/56070/R | 38016 | 440 | 17700 | 10 | 15 | 25 | 45 |  | 78211 | 15983 | 17700 | #REF! | #REF! | #REF! | #REF! | TBC | 94.3089
Edgmond | 370600 | 319700 | 2389.6 |  | Z | =Z/2.4 |  |  |  | AMP6 quality improvement scheme - will incorporate any capacity increases required | Trib of River Strine |  | S/04/56016/R | 1503.36 | 17.4 | 5900 | 3 |  | 15 | 30 |  | 2356 | 348 | - | #REF! | #REF! | #REF! | #REF! | TBC | 0
Monkmoor |  |  | 94134 |  | Z | =Z/2.14 |  |  |  | growth insignificant | River Severn |  | S/02/56373/R | 85363 | 987.9977 | 20838 | 10 |  | 25 | 45 |  | - | - | - | #REF! | #REF! | #REF! | #REF! | TBC | 0
Newport | 373700 | 319200 | 13309.6 |  | Z | =Z/2.4 |  |  |  | Project to transfer part of the catchment to Rushmoor in AMP6 | Strine Brook |  | S/04/09049/R | 5866.6 | 67.9005 | 2500 | 3 |  | 15 | 20 | 2 | 12940 | 2256 | 2500 | #REF! | #REF! | #REF! | #REF! | TBC | 78.9295
Rushmoor | 361731 | 313381 | 103247.2 |  | Z | =Z/2.4 |  |  |  |  | River Tern |  | S/04/55141/R | 61542.7 | 712.2998 | 23523 | 5 | 7 | 15 | 30 | 1 | 98140 | 15895 | 23523 | #REF! | #REF! | #VALUE! | #REF! | TBC | 592.0054
Waters Upton | 363165 | 319381 | 221.2 |  | Z | =Z/2.5 |  |  |  | sewage works closed - pumped to Rushmoor | River Tern | [10 empty] | I've had to calculate - they haven't confirmed |  | So no change | #REF! | #REF! | #REF! | #REF! | TBC | 0
Little Wenlock | 364400 | 306300 | 0 |  | Z | =Z/2.4 |  |  |  |  | Rtrib of River Severn | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Great Bolas | 365032 | 321638 | 0 |  | Z | =Z/2.4 |  |  |  |  | Trib of River Tern | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Crudgington | 363300 | 318000 | 48 |  | Z | =Z/2.6 |  |  |  |  | River Strine | [13 empty] | 0 | 0 | 0 | 0 | TBC | 240.9892
Cherrington | 428900 | 237000 | 0 |  | Z | =Z/2.7 |  |  |  |  | River Stour | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Roden | 357500 | 316900 | 0 |  | Z | =Z/2.8 |  |  |  |  | River Roden | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
High Ercall | 359500 | 316400 | 754.8 |  | Z | =Z/2.9 |  |  |  |  | Trib of River Roden | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Osbaston | 360800 | 319400 | 0 |  | Z | =Z/2.10 |  |  |  |  | Lakemoor Brook | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Ellerdine | 362100 | 321100 | 96 |  | Z | =Z/2.11 |  |  |  |  | Lakemoor Brook | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Walcote | 359600 | 312200 | 84 |  | Z | =Z/2.12 |  |  |  |  | Trib of River Tern | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Sambrook | 371400 | 323800 | 148 |  | Z | =Z/2.13 |  |  |  |  | River Meese | [13 empty] | 0 | 0 | 0 | 0 | TBC | 0
Sugden |  |  | 52 |  | Z | =Z/2.15 | [18 empty] | 0 | 0 | 0 | 0 | TBC | 0
Coalport
| Year | pDWF | Q80 | Q90 | Days
| 2011 | 17700 | 12558 | 12330 | 365
| 2012 | 17700 | 15932 | 14868 | 364
| 2013 | 17700 | 13010 | 11320 | 363
| 2014 | 17700 | 11550 | 10640 | 362
| AVE |  | 13262.5 | 12289.5
Edgmond
| Year | pDWF | Q80 | Q90 | Days
| 2011 | 590 | 401 | 371 | 359
| 2012 | 590 | 460 | 396 | 340
| 2013 | 590 | 417 | 376 | 346
| 2014 | 590 | 546 | 465 | 364
| AVE |  | 456 | 402
Monkmoor
| Year | pDWF | Q80 | Q90 | Days
| 2011 | 20838 | 16060 | 15590 | 357
| 2012 | 20838 | 18860 | 17490 | 364
| 2013 | 20838 | 18350 | 17410 | 364
| 2014 | 20838 | 19260 | 17890 | 365
| AVE |  | 18132.5 | 17095
Newport
| Year | pDWF | Q80 | Q90 | Days
| 2011 | 2500 | 1916 | 1872 | 364
| 2012 | 2500 | 2106 | 2033 | 365
| 2013 | 2500 | 2264 | 2083 | 365
| 2014 | 2500 | 2516 | 2381 | 365
| AVE |  | 2200.5 | 2092.25
Rushmoor
| Year | pDWF | Q80 | Q90 | Days
| 2011 | 23523 | 13670 | 12320 | 356
| 2012 | 23523 | 18050 | 17230 | 320
| 2013 | 23523 | 20900 | 18500 | 202
| 2014 | 23523 | 18517 | 17456 | 363
| AVE |  | 17784.25 | 16376.5
Note on D18: sandra.ryan: Value as per 2010 + completions since then (does not include 2015 un der construction).
Note on O19: mcraig1: This should really be expressed in l/s not m3/d. It is an instantaneous conditon, not daily total
Note on Q21: sandra.ryan: Incoming listed as 5900 - typo? Support table shows 590
General comment regarding treatment capacity:
Whilst sewage treatment works may not have sufficient spare capacity to accept the levels of development being proposed in its catchment area this does not necessarily mean that development cannot take place. Under Section 94 of the Water Industry Act 1991 sewerage undertakers have an obligation to provide additional treatment capacity as and when required. Where necessary we will discuss any discharge consent implications with the Environment Agency. If there are specific issues which may prevent or delay the provision on additional capacity these have been highlighted below.

## New developments to model
[5 empty] | (Shelton) Occupancy: | 2.4947 |  | 2.3472
2.421
[5 empty] | mPCC | 115
Potential impact of proposed developments on sewerage infrastructure assets |  |  |  |  | Factor to waste | 0
Note: These are desktop assessments using readily available information and have not been subjected to detailed hydraulic modelling
Site Ref | Status | Status | Site Ward | Size | Units (no of dwellings) | Additional m3/d to WwTW | Additional l/s to WwTW | Sewage Treatment Works Catchment | Sewerage Comment | Potential impact on sewerage infrastructure
residential | Not Started | Committed | Cuckoo Oak |  | 2 | 0.55682 | 0.0064447 | Coalport
residential | Not Started | Committed | Dawley Magna |  | 349 | 97.1652 | 1.1246 | Coalport
residential | Not Started | Committed | Horsehay & Lightmoor |  | 1076 | 299.5695 | 3.4672 | Coalport
residential | Not Started | Committed | Ironbridge Gorge |  | 111 | 30.9035 | 0.35768 | Coalport
residential | Not Started | Committed | Ketley and Oakengates |  | 2 | 0.55682 | 0.0064447 | Coalport
residential | Not Started | Committed | Lawley and Overdale |  | 94 | 26.1706 | 0.3029 | Coalport
residential | Not Started | Committed | Madeley |  | 22 | 6.125 | 0.070892 | Coalport
residential | Not Started | Committed | Malinslee |  | 176 | 49.0002 | 0.56713 | Coalport
residential | Not Started | Committed | Priorslee |  | 1041 | 289.8251 | 3.3545 | Coalport
residential | Not Started | Committed | The Nedge |  | 81 | 22.5512 | 0.26101 | Coalport
residential | Not Started | Committed | Woodside |  | 163 | 45.3809 | 0.52524 | Coalport
residential | Resolution to Grant | Committed | The Gorge |  | 12 | 3.3409 | 0.038668 | Coalport
residential | Resolution to Grant | Committed | Dawley Hamlets |  | 13 | 3.6193 | 0.04189 | Coalport
residential | Under Construction | Committed | Brookside |  | 18 | 5.0114 | 0.058002 | Coalport
residential | Under Construction | Committed | Cuckoo Oak |  | 44 | 12.2501 | 0.14178 | Coalport
residential | Under Construction | Committed | Dawley Magna |  | 15 | 4.1762 | 0.048335 | Coalport
residential | Under Construction | Committed | Horsehay & Lightmoor |  | 21 | 5.8466 | 0.067669 | Coalport
residential | Under Construction | Committed | Ironbridge Gorge |  | 8 | 2.2273 | 0.025779 | Coalport
residential | Under Construction | Committed | Madeley |  | 21 | 5.8466 | 0.067669 | Coalport
residential | Under Construction | Committed | Malinslee |  | 13 | 3.6193 | 0.04189 | Coalport
residential | Under Construction | Committed | Woodside |  | 64 | 17.8183 | 0.20623 | Coalport
residential | Not Started | Committed | Edgmond |  | 52 | 14.4773 | 0.16756 | Edgmond
residential | Resolution to Grant | Committed | Tibberton & Cherrington |  | 22 | 6.125 | 0.070892 | Edgmond
residential | Not Started | Committed | Wrockwardine |  | 25 | 6.9603 | 0.080559 | Monkmoor
residential | Not Started | Committed | Church Aston and Lilleshall |  | 66 | 18.3751 | 0.21267 | Newport
residential | Not Started | Committed | Edgmond |  | 103 | 28.6763 | 0.3319 | Newport
residential | Not Started | Committed | Newport East |  | 2 | 0.55682 | 0.0064447 | Newport
residential | Not Started | Committed | Newport South |  | 102 | 28.3979 | 0.32868 | Newport
residential | Not Started | Committed | Newport West |  | 209 | 58.1878 | 0.67347 | Newport
residential | Not Started | Committed | Newport North |  | 46 | 12.8069 | 0.14823 | Newport
residential | Resolution to Grant | Committed | Newport South |  | 350 | 97.4436 | 1.1278 | Newport
residential | Resolution to Grant | Committed | Newport South |  | 215 | 59.8582 | 0.6928 | Newport
residential | Resolution to Grant | Committed | Chetwynd Aston |  | 51 | 14.1989 | 0.16434 | Newport
residential | Under Construction | Committed | Edgmond |  | 5 | 1.3921 | 0.016112 | Newport
residential | Under Construction | Committed | Newport East |  | 1 | 0.27841 | 0.0032223 | Newport
residential | Under Construction | Committed | Newport South |  | 34 | 9.466 | 0.10956 | Newport
residential | Under Construction | Committed | Newport West |  | 59 | 16.4262 | 0.19012 | Newport
residential | Resolution to Grant | Committed | Wrockwardine |  | 470 | 130.8528 | 1.5145 | None - nearest would be Rushmoor
residential | Not Started | Committed | Apley Castle |  | 105 | 29.2331 | 0.33835 | Rushmoor
residential | Not Started | Committed | Arleston |  | 240 | 66.8185 | 0.77336 | Rushmoor
residential | Not Started | Committed | Church Aston and Lilleshall |  | 40 | 11.1364 | 0.12889 | Rushmoor
residential | Not Started | Committed | College |  | 70 | 19.4887 | 0.22556 | Rushmoor
residential | Not Started | Committed | Donnington |  | 45 | 12.5285 | 0.14501 | Rushmoor
residential | Not Started | Committed | Dothill |  | 19 | 5.2898 | 0.061224 | Rushmoor
residential | Not Started | Committed | Ercall |  | 99 | 27.5626 | 0.31901 | Rushmoor
residential | Not Started | Committed | Ercall Magna |  | 9 | 2.5057 | 0.029001 | Rushmoor
residential | Not Started | Committed | Hadley and Leegomery |  | 336 | 93.5459 | 1.0827 | Rushmoor
residential | Not Started | Committed | Haygate |  | 167 | 46.4945 | 0.53813 | Rushmoor
residential | Not Started | Committed | Horsehay & Lightmoor |  | 161 | 44.8241 | 0.5188 | Rushmoor
residential | Not Started | Committed | Ketley and Oakengates |  | 327 | 91.0402 | 1.0537 | Rushmoor
residential | Not Started | Committed | Lawley and Overdale |  | 2409 | 670.6904 | 7.7626 | Rushmoor
residential | Not Started | Committed | Muxton |  | 31 | 8.6307 | 0.099893 | Rushmoor
residential | Not Started | Committed | Park |  | 19 | 5.2898 | 0.061224 | Rushmoor
residential | Not Started | Committed | Priorslee |  | 111 | 30.9035 | 0.35768 | Rushmoor
residential | Not Started | Committed | St. Georges |  | 198 | 55.1252 | 0.63802 | Rushmoor
residential | Not Started | Committed | Wrockwardine |  | 25 | 6.9603 | 0.080559 | Rushmoor
residential | Not Started | Committed | Wrockwardine Wood and Trench |  | 79 | 21.9944 | 0.25456 | Rushmoor
residential | Not Started | Committed | Priorslee |  | 120 | 33.4092 | 0.38668 | Rushmoor
residential | Resolution to Grant | Committed | Hadley |  | 540 | 150.3416 | 1.7401 | Rushmoor
residential | Under Construction | Committed | Apley Castle |  | 20 | 5.5682 | 0.064447 | Rushmoor
residential | Under Construction | Committed | Arleston |  | 9 | 2.5057 | 0.029001 | Rushmoor
residential | Under Construction | Committed | Church Aston and Lilleshall |  | 1 | 0.27841 | 0.0032223 | Rushmoor
residential | Under Construction | Committed | College |  | 13 | 3.6193 | 0.04189 | Rushmoor
residential | Under Construction | Committed | Donnington |  | 11 | 3.0625 | 0.035446 | Rushmoor
residential | Under Construction | Committed | Ercall |  | 96 | 26.7274 | 0.30934 | Rushmoor
residential | Under Construction | Committed | Ercall Magna |  | 6 | 1.6705 | 0.019334 | Rushmoor
residential | Under Construction | Committed | Hadley and Leegomery |  | 123 | 34.2445 | 0.39635 | Rushmoor
residential | Under Construction | Committed | Haygate |  | 10 | 2.7841 | 0.032223 | Rushmoor
residential | Under Construction | Committed | Horsehay & Lightmoor |  | 69 | 19.2103 | 0.22234 | Rushmoor
residential | Under Construction | Committed | Ketley and Oakengates |  | 137 | 38.1422 | 0.44146 | Rushmoor
residential | Under Construction | Committed | Lawley and Overdale |  | 51 | 14.1989 | 0.16434 | Rushmoor
residential | Under Construction | Committed | Muxton |  | 6 | 1.6705 | 0.019334 | Rushmoor
residential | Under Construction | Committed | Priorslee |  | 16 | 4.4546 | 0.051557 | Rushmoor
residential | Under Construction | Committed | St. Georges |  | 5 | 1.3921 | 0.016112 | Rushmoor
residential | Under Construction | Committed | Wrockwardine |  | 14 | 3.8977 | 0.045113 | Rushmoor
residential | Under Construction | Committed | Wrockwardine Wood and Trench |  | 5 | 1.3921 | 0.016112 | Rushmoor
residential | Resolution to Grant | Committed | Waters Upton |  | 7 | 1.9489 | 0.022556 | Waters Upton
Employment | Completed | Completed | Dawley Hamlets |  | - | -0.8 | -0.0092593 | Coalport | m3/day from employment sites converted from development size (Gross area converted to to Net Internal Area) and estimated typical FTE as appropriate to the development site Class Use (assumes 16 litres/FTE/day).
Employment | Completed | Completed | Great Dawley |  | - | 2.608 | 0.030185 | Coalport | Negative values returned where the development plans include the closure of previous (within the last 3 months) employment sites, i.e. representing a cessation in demand.
Employment | Completed | Completed | Hollinswood and Randlay |  | - | 0.864 | 0.01 | Coalport
Employment | Completed | Completed | Lawley and Overdale |  | - | 10.24 | 0.11852 | Coalport
Employment | Completed | Completed | Lilleshall and Donnington |  | - | 0.144 | 0.0016667 | Coalport
Employment | Completed | Completed | Madeley |  | - | 3.92 | 0.04537 | Coalport
Employment | Completed | Completed | St Georges and Priorslee |  | - | 0.256 | 0.002963 | Coalport
Employment | Completed | Completed | Stirchley and Brookside |  | - | 0.208 | 0.0024074 | Coalport
Employment | Completed | Completed | The Gorge |  | - | 0.016 | 0.00018519 | Coalport
Employment | Completed | Completed | Church Aston |  | - | 0.272 | 0.0031481 | Edgmond
Employment | Completed | Completed | Tibberton and Cherrington |  | - | 0.192 | 0.0022222 | Edgmond
Employment | Completed | Completed | Chetwynd Aston |  | - | 0.128 | 0.0014815 | Newport
Employment | Completed | Completed | Church Aston |  | - | 4.88 | 0.056481 | Newport
Employment | Completed | Completed | Newport |  | - | -0.512 | -0.0059259 | Newport
Employment | Completed | Completed | Dawley Hamlets |  | - | 0.048 | 0.00055556 | Rushmoor
Employment | Completed | Completed | Hadley |  | - | 8.752 | 0.1013 | Rushmoor
Employment | Completed | Completed | Ketley |  | - | 0.672 | 0.0077778 | Rushmoor
Employment | Completed | Completed | Lawley and Overdale |  | - | 0 | 0 | Rushmoor
Employment | Completed | Completed | Lilleshall and Donnington |  | - | -0.336 | -0.0038889 | Rushmoor
Employment | Completed | Completed | Oakengates |  | - | 0.096 | 0.0011111 | Rushmoor
Employment | Completed | Completed | Wellington |  | - | -1.184 | -0.013704 | Rushmoor
Employment | Completed | Completed | Wrockwardine |  | - | -0.016 | -0.00018519 | Rushmoor
Employment | Completed | Completed | Wrockwardine Wood and Trench |  | - | 3.072 | 0.035556 | Rushmoor
Employment | Completed | Completed | Chetwynd |  | - | -0.304 | -0.0035185 | Sambrook
Employment | Committed | Committed | Dawley Hamlets |  | - | -0.336 | -0.0038889 | Coalport
Employment | Committed | Committed | Great Dawley |  | - | -0.032 | -0.00037037 | Coalport
Employment | Committed | Committed | Hollinswood and Randlay |  | - | -2.4 | -0.027778 | Coalport
Employment | Committed | Committed | Lawley and Overdale |  | - | 3.312 | 0.038333 | Coalport
Employment | Committed | Committed | Lilleshall and Donnington |  | - | 0.064 | 0.00074074 | Coalport
Employment | Committed | Committed | Little Wenlock |  | - | 0.256 | 0.002963 | Coalport
Employment | Committed | Committed | Madeley |  | - | -6.016 | -0.06963 | Coalport
Employment | Committed | Committed | St George and Priorslee |  | - | 2.96 | 0.034259 | Coalport
Employment | Committed | Committed | Stirchley and Brookside |  | - | -0.88 | -0.010185 | Coalport
Employment | Committed | Committed | The Gorge |  | - | -0.752 | -0.0087037 | Coalport
Employment | Committed | Committed | Chetwynd |  |  | 0 | 0 | Edgmond
Employment | Committed | Committed | Edgmond |  |  | 0.576 | 0.0066667 | Edgmond
Employment | Committed | Committed | Tibberton and Cherrington |  |  | 0.016 | 0.00018519 | Edgmond
Employment | Committed | Committed | Rodington |  |  | -0.912 | -0.010556 | Monkmoor
Employment | Committed | Committed | Chetwynd Aston |  |  | 1.664 | 0.019259 | Newport
Employment | Committed | Committed | Newport |  |  | 4.8 | 0.055556 | Newport
Employment | Committed | Committed | Ercall Magna |  |  | 0.32 | 0.0037037 | Roden
Employment | Committed | Committed | Eyton Upon the Weald Moors |  |  | 0.032 | 0.00037037 | Rushmoor
Employment | Committed | Committed | Great Dawley |  |  | -0.016 | -0.00018519 | Rushmoor
Employment | Committed | Committed | Hadley |  |  | -1.584 | -0.018333 | Rushmoor
Employment | Committed | Committed | Ketley |  |  | 0.384 | 0.0044444 | Rushmoor
Employment | Committed | Committed | Kynnersley |  |  | -0.944 | -0.010926 | Rushmoor
Employment | Committed | Committed | Lawley and Overdale |  |  | 0.592 | 0.0068519 | Rushmoor
Employment | Committed | Committed | Lilleshall and Donnington |  |  | -0.336 | -0.0038889 | Rushmoor
Employment | Committed | Committed | Oakengates |  |  | 2.896 | 0.033519 | Rushmoor
Employment | Committed | Committed | Preston Upon The Weald Moors |  |  | -0.032 | -0.00037037 | Rushmoor
Employment | Committed | Committed | Rodington |  |  | 0.016 | 0.00018519 | Rushmoor
Employment | Committed | Committed | St George and Priorslee |  |  | -0.08 | -0.00092593 | Rushmoor
Employment | Committed | Committed | Waters Upton |  |  | 0.016 | 0.00018519 | Rushmoor
Employment | Committed | Committed | Wellington |  |  | 2.64 | 0.030556 | Rushmoor
Employment | Committed | Committed | Wrockwardine |  |  | -0.096 | -0.0011111 | Rushmoor
Employment | Committed | Committed | Wrockwardine Wood and Tench |  |  | 0.736 | 0.0085185 | Rushmoor
Employment | Committed | Committed | Chetwynd |  |  | -0.032 | -0.00037037 | Sambrook
Employment | Committed | Committed | Wrockwardine |  |  | 0 | 0 | Walcot
Employment | Committed | Committed | Waters Upton |  |  | 0.048 | 0.00055556 | Waters Upton
residential | Allocated | Allocated | Dawley Magna |  | 240 | 66.8185 | 0.77336 | Coalport
residential | Allocated | Allocated | Horsehay & Lightmoor |  | 40 | 11.1364 | 0.12889 | Coalport
residential | Allocated | Allocated | Ironbridge Gorge |  | 106 | 29.5115 | 0.34157 | Coalport
residential | Allocated | Allocated | Lawley and Overdale |  | 70 | 19.4887 | 0.22556 | Coalport
residential | Allocated | Allocated | Madeley |  | 54 | 15.0342 | 0.17401 | Coalport
residential | Allocated | Allocated | Newport |  | 120 | 33.4092 | 0.38668 | Coalport
residential | Allocated | Allocated | Priorslee |  | 1100 | 306.2513 | 3.5446 | Coalport
residential | Allocated | Allocated | Brookside |  | 321 | 89.3697 | 1.0344 | Coalport
residential | Allocated | Allocated | Donnington |  | 750 | 208.8077 | 2.4168 | Rushmoor
residential | Allocated | Allocated | Dothill |  | 215 | 59.8582 | 0.6928 | Rushmoor
residential | Allocated | Allocated | Lawley and Overdale |  | 250 | 69.6026 | 0.80559 | Rushmoor
residential | Allocated | Allocated | Priorslee |  | 110 | 30.6251 | 0.35446 | Rushmoor
residential | Allocated | Allocated | Wrockwardine Wood and Trench |  | 123 | 34.2445 | 0.39635 | Rushmoor
Employment | Allocated | Allocated | Hadley |  | 65 | 18.0967 | 0.20945 | Coalport
Employment | Allocated | Allocated | Madeley |  | 29 | 8.0739 | 0.093448 | Coalport
Employment | Allocated | Allocated | Madeley |  | 13 | 3.6193 | 0.04189 | Newport
Employment | Allocated | Allocated | Chetwynd Aston |  | 66 | 18.3751 | 0.21267 | Newport
Employment | Allocated | Allocated | Hadley |  | 320 | 89.0913 | 1.0311 | Rushmoor
Employment | Allocated | Allocated | Wrockwardine & Trench |  | 26 | 7.2387 | 0.083781 | Rushmoor
Employment | Allocated | Allocated | Lilleshall & Donnington |  | 41 | 11.4148 | 0.13212 | Rushmoor
Employment | Allocated | Allocated | Oakengates |  | 21 | 5.8466 | 0.067669 | Rushmoor
Employment | Allocated | Allocated | Lawley & Overdale |  | 8 | 2.2273 | 0.025779 | Rushmoor
Employment | Allocated | Allocated | Madeley |  | 25 | 6.9603 | 0.080559 | Rushmoor
Employment | Allocated | Allocated | Eyton |  | 151 | 42.04 | 0.48657 | Rushmoor
Employment | Allocated | Allocated | Hollinswood & Randley |  | 240.9892 | 67.0939 | 0.77655 | Crudgington
Pressure on | Rushmoor
Completed | Employment |  |  |  |  | 11.104 | 0.12852
Committed | residential |  |  |  |  | 1598.632 | 18.5027
Committed | Employment |  |  |  |  | 4.224 | 0.048889
sub total - committed pressure | [5 empty] | 1613.96 | 18.6801
Allocated | residential |  |  |  |  | 403.1381 | 4.666
Allocated | Employment |  |  |  |  | 164.8189 | 1.9076
Total (all pressure): | [5 empty] | 3795.8771 | 43.9338
Pressure on | Coalport
Completed | Employment |  |  |  |  | 17.456 | 0.20204
Committed | residential |  |  |  |  | 931.5609 | 10.782
Committed | Employment |  |  |  |  | -3.824 | -0.044259
sub total - committed pressure | [5 empty] | 945.1929 | 10.9397
Allocated | residential |  |  |  |  | 571.0196 | 6.609
Allocated | Employment |  |  |  |  | 26.1706 | 0.3029
Total (all pressure): | [5 empty] | 2487.5759 | 28.7914
Pressure on | Newport
Completed | Employment |  |  |  |  | 4.496 | 0.052037
Committed | residential |  |  |  |  | 346.064 | 4.0054
Committed | Employment |  |  |  |  | 6.464 | 0.074815
sub total - committed pressure | [5 empty] | 357.024 | 4.1322
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 21.9944 | 0.25456
Total (all pressure): | [5 empty] | 379.0184 | 4.3868
Pressure on | Edgmond
Completed | Employment |  |  |  |  | 0.464 | 0.0053704
Committed | residential |  |  |  |  | 20.6024 | 0.23845
Committed | Employment |  |  |  |  | 0.592 | 0.0068519
sub total - committed pressure | [5 empty] | 21.6584 | 0.25068
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 0 | 0
Total (all pressure): | [5 empty] | 21.6584 | 0.25068
Pressure on | Monkmoor
Completed | Employment |  |  |  |  | 0 | 0
Committed | residential |  |  |  |  | 6.9603 | 0.080559
Committed | Employment |  |  |  |  | -0.912 | -0.010556
sub total - committed pressure | [5 empty] | 6.0483 | 0.070003
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 0 | 0
Total (all pressure): | [5 empty] | 6.0483 | 0.070003
Pressure on | Waters Upton
Completed | Employment |  |  |  |  | 0 | 0
Committed | residential |  |  |  |  | 1.9489 | 0.022556
Committed | Employment |  |  |  |  | 0.048 | 0.00055556
sub total - committed pressure | [5 empty] | 1.9969 | 0.023112
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 0 | 0
Total (all pressure): | [5 empty] | 1.9969 | 0.023112
Pressure on | Sambrook
Completed | Employment |  |  |  |  | -0.304 | -0.0035185
Committed | residential |  |  |  |  | 0 | 0
Committed | Employment |  |  |  |  | -0.032 | -0.00037037
sub total - committed pressure | [5 empty] | -0.336 | -0.0038889
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 0 | 0
Total (all pressure): | [5 empty] | -0.336 | -0.0038889
Pressure on | Roden
Completed | Employment |  |  |  |  | 0 | 0
Committed | residential |  |  |  |  | 0 | 0
Committed | Employment |  |  |  |  | 0.32 | 0.0037037
sub total - committed pressure | [5 empty] | 0.32 | 0.0037037
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 0 | 0
Total (all pressure): | [5 empty] | 0.32 | 0.0037037
Pressure on | Walcot
Completed | Employment |  |  |  |  | 0 | 0
Committed | residential |  |  |  |  | 0 | 0
Committed | Employment |  |  |  |  | 0 | 0
sub total - committed pressure | [5 empty] | 0 | 0
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 0 | 0
Total (all pressure): | [5 empty] | 0 | 0
Pressure on | Crudgington
Completed | Employment |  |  |  |  | 0 | 0
Committed | residential |  |  |  |  | 0 | 0
Committed | Employment |  |  |  |  | 0 | 0
sub total - committed pressure | [5 empty] | 0 | 0
Allocated | residential |  |  |  |  | 0 | 0
Allocated | Employment |  |  |  |  | 67.0939 | 0.77655
Total (all pressure): | [5 empty] | 67.0939 | 0.77655
Note on F3: sandra.ryan: New homes will be metered
Note on F159: sandra.ryan: Calculated from ha (estimated FTE based on Use Class, and FTE * 16l/h/d, converted into dwellings equivalent.
Note on G1: sandra.ryan: Total population / total hh props (excl voids) - from WRMP table 2010
Note on G3: sandra.ryan: 120 dropping to 110 by 2025/26
Note on I1: sandra.ryan: 2025/26

## Image
Coalport WwTW catchment
Rushmoor WwTW catchment
Waters Upton WwTW catchment
Newport WwTW catchment
Edgmond WwTW catchment
Crudgington WwTW catchment
Monkmoor WwTW catchment